## Slide 1: Earthing Issues at El Roque de los Muchachos Observatory
UCM-ELEC
July 2020
UCM-ELEC
Madrid, 24th July
Silvia Ronda, Oibar Martinez, Clara Oliver, Patricia Marquez and Jose Miguel Miranda

## Slide 2: Main topics
          Why Earthing?
          The importance of soil resistivity and its influence in earth resistance value
          Representative situations in ORM
          How to improve Earthing systems

## Slide 3: Earthing
Earth Resistance: “Resistance between the electrode and the point of zero potential (the infinite earth)”
Earthing System: Conducting connection between an electrical circuit and the Earth to prevent damage in the case of high discharges. It should be AS LOW AS POSSIBLE. Standards recommend < 10 Ω (low frequency) [IEC-62305-3]. It is influenced by:
          Resistance of the electrodes
          Contact resistance between electrode and soil
          Resistivity of the soil
S
[]=Ohm·m
[R]=Ohm
Depends on the material only
Depends on the material and geometry

## Slide 4: Soil resistivity
Resistivity depends on the type of soil
Volcanic terrain
ORM
Geotechnical studies

## Slide 5: Soil resistivity measurement: Wenner Method
4 electrodes method
Equipotential surface
Current density lines
Layer 1 | σ=1e-3
Layer 2 | σ=2e-3
Layer 3 | σ=3e-3
Equipotential surfaces
Current density lines and direction
Simulations with COMSOL
Voltage
5

## Slide 6: Soil resistivity measurement in ORM
Site | (kΩ m) | 
MAGIC I | 0.57 | Homogeneous
MAGIC II | 0.53 | Homogeneous
LST1 | 1.44 | Homogeneous
LST2 | 4.3-6.1 | Non-Homog.
LST3 | 1.7-11.5 | Non-Homog.
LST4 | 2.45 | Homogeneous
Site |  | 
MAGIC I | 0.57 | Homogeneous
MAGIC II | 0.53 | Homogeneous
LST1 | 1.44 | Homogeneous
LST2 | 4.3-6.1 | Non-Homog.
LST3 | 1.7-11.5 | Non-Homog.
LST4 | 2.45 | Homogeneous
Soil resistivity measurements made in ORM. The numbers correspond to the interelectrode distance in m, roughly equal to depth.
Soil resistivity measurements made in ORM. The numbers correspond to the interelectrode distance in m.
Soil resistivity measurements made in ORM. The numbers correspond to the interelectrode distance in m.

## Slide 7: Representative situations in ORM
HOMOGENEOUS HIGH RESISTIVITY SOIL
LST1
1.44 kΩ m
NON HOMOGENEOUS SOIL WITH VERY HIGH RESISTIVITY LAYERS
LST3
3.5 kΩ m
1.5 kΩ m
15.4 kΩ m
18.4 kΩ m
Voltage distribution when resistivity is measured with Wenner method

## Slide 8: Possible solutions to reduce earth resistance
          Chemical treatment of soil or use low resistivity materials
          Burying metal grids plates (horizontal)
          Electrodes driven vertical into the ground
          Electrodes or Earthing Systems interconnection
Design in COMSOL for optimizing the telescopes Earthing
  (1) Soil
  (2) Infinite Element Domain Layer
  (3) Extra fine mesh zone surrounding earth resistance structure
  (4) Earth resistance structure
  (5) Ground

## Slide 9: Burying metal plates (horizontal and vertical)
 | 69.2 Ω
 | 53.5 Ω
 | 25.5 Ω
53.5 m
HOMOGENEOUS SOIL
NON HOMOGENEOUS SOIL
 | 15.2 Ω
 | 11.0 Ω
 | 7.1 Ω
Voltage distribution
max
 | 27.9Ω
 | 23.6 Ω
7 vertical electrodes
22 vertical electrodes
53.5 m

## Slide 10: Burying vertical electrodes in homogeneous soil
R= 7.06Ω
R= 7.14Ω
R= 6.79Ω
R= 6.54Ω
R= 6.31Ω
R= 6.43Ω
R= 6.21Ω
R= 6.01Ω
Chart: Number of vertical electrodes
| 0 | 2 | 4 | 6 | 8 | 10 | 12 | 16
Valores Y | 7.14 | 7.05 | 6.79 | 6.55 | 6.43 | 6.31 | 6.21 | 6.01
10 m
53.5 m
HOMOGENEOUS HIGH RESISTIVITY SOIL

## Slide 11
Earthing systems connected
Ω
If the resistances work as if they are pararell connected the value expected if we interconnet two LST1 is:
Electrodes or Earthing Systems interconnection
R= 8.58 Ω
R= 16.64 Ω
No connected
Connected
This is verifyed with simulation in LST1 (homogeneous soil)

## Slide 12
LST1
LST3
Soil conductivity
LST1
LST3
No connected
̴15.2 Ω
̴69.2 Ω
Ω
Electrodes or Earthing Systems interconnection
Expected value for earth resistance of LST1-LST3 interconnection:
11.6 Ω
70.7 Ω
Simulation of the resitance in LST3
No connected
Connected

## Slide 13
Solution | Homogeneous soil (LST1) | Non- homogeneous soil (LST3)
Low resistivity materials or chemical treatment |  | 
Burying metal grids or plates (horizontal) |  | 
Vertical electrodes buried into the ground |  | 
Electrodes or earthing systems interconnection |  | 
Possible solutions to lowering earth resistance
Soil resistivity is necessary when determining the design of the grounding system for new installations.
Poor soil conditions (high resistivity) can be overcome with specific grounding designs.
Our findings might help to efficiently design the future ground structures for the installations under construction and are applicable to other similar sites with soils of volcanic nature.

## Slide 14
Thank You